Plant & Machinery Monitoring System

User Manual

| Filling Reference : | Integra/AMU/KIT6/User Manual |  |
| --- | --- | --- |
| Document Title : | User Manual |  |
| Version : | Draft |  |
| Document Author: | Mr. Sabarish |  |
| Date Created : | 01/06/2025 |  |
| Date Modified : | 01/06/2025 |  |

|  | Reviewed By | Accepted By |
| --- | --- | --- |
| Signature & Date |  |  |
| Name | Mr. Bala |  |
| Designation | Technical Consultant |  |

Change History:

| Version | Date | Author | Change History |
| --- | --- | --- | --- |
| Draft | 01/06/2025 | Mr. Sabarish | Initial Draft Created |

Distribution List:

| Name | Email Address |
| --- | --- |
| Mr. Bala | bala@integratech.com.sg |
| Mr. Hari | hari@integratech.com.sg |
| Mr. Selva Pandian | selvapandian@integratech.com.sg |
| Mr. Sabarish | sabarish@integratech.com.sg |
| Mr. Sivaguru | sivaguru@integratech.com.sg |

Table of Contents

| Table of Contents 1. Project Overview 4 2. Objectives 4 3. Hardware Component 5 4. Software Component 6 5. Circuit Diagram and Wiring 7 6. Code Explanation 10 7. Setup and Usage Instructions 11 8. Data Flow and Communication 12 9. Troubleshooting and FAQs 13 10. Sample Code 14 Class 1: DHT11 + TFT Display 14 Class 2: NTC Thermistor + TFT Display 15 Class 3: PZEM004T (Voltage, Current) + TFT Display 16 Class 4: ADP810 Differential Pressure + TFT Display 17 Class 5: HX710B Air Pressure Sensor + TFT Display 18 Class 6: DHT11 + NTC Thermistor + TFT Display 20 Class 7: PZEM004T + ADP810 Differential Pressure + TFT Display 21 Class 8: HX710B + Flow Sensor + TFT Display 23 Class 9: DHT11 + PZEM004T + Relay Status + TFT Display 24 Class 10: ADP810 + HX710B + Flow Sensor + TFT Display 26 Class 11: DHT11 + ADP810 Pressure + TFT Display 28 Class 12: NTC Thermistor + Flow Sensor + TFT Display 30 Class 13: PZEM004T Energy Monitor + DHT11 + TFT Display 32 Class 14: HX710B Pressure Sensor + Flow Sensor + TFT Display 33 Class 15: NTC Thermistor + HX710B + TFT Display 35 Class 16: DHT11 + PZEM004T + Flow Sensor + TFT Display 37 Class 17: NTC Thermistor + ADP810 + Flow Sensor + TFT Display 39 Class 18: DHT11 + HX710B + PZEM004T + TFT Display 41 Class 19: ADP810 + Flow Sensor + PZEM004T + TFT Display 43 Class 20: DHT11 + NTC Thermistor + HX710B + TFT Display 46 |  |
| --- | --- |

- Project Overview

This project implements a comprehensive monitoring and control system for plant and machinery environments using the ESP32 microcontroller. It integrates multiple sensors to measure environmental and electrical parameters, displays data on a TFT screen, and transmits it to both a ThingsBoard server and a Flask-based API.

- Objectives

- Monitor real-time temperature, humidity, voltage, current, flow rate, and pressure.

- Automatically control a water motor based on water level.

- Display sensor readings on a TFT screen.

- Upload telemetry data securely to ThingsBoard and locally to a Flask API.

- Support OTA firmware updates for remote maintenance.

- Hardware Component

| Component | Description |
| --- | --- |
| ESP32 Dev Board | Main controller with Wi-Fi and Bluetooth |
| DHT11 Sensor | Temperature and humidity sensing |
| PZEM004T v3.0 | Electrical parameter monitoring |
| ADP810 | Differential pressure sensor via I²C |
| HX710B + Pressure Sensor | Air pressure reading through ADC |
| NTC Thermistor | Water temperature monitoring |
| Water Flow Sensor | Measures water flow rate |
| Relay Module | Controls motor based on water level |
| TFT_22_ILI9225 Display | Displays sensor data on screen |
| Power Supply | 5V or 3.3V depending on board and sensors |

- Software Component

| Software/Library | Purpose |
| --- | --- |
| Arduino Core for ESP32 | Firmware development |
| WiFiManager | Simplifies Wi-Fi configuration |
| ArduinoOTA | Enables OTA updates |
| DHT | Interface for DHT11 |
| PZEM004Tv30 | Communication with PZEM module |
| ArduinoJson | Create and parse JSON data |
| HTTPClient + WiFiClientSecure | HTTP/HTTPS POST requests |
| TFT_22_ILI9225 | Display handling |

- Circuit Diagram and Wiring

Main Connections

| Sensor / Module | ESP32 Pin |
| --- | --- |
| DHT11 | GPIO 4 |
| Water Flow Sensor | GPIO 17 |
| HX710B OUT | GPIO 21 |
| HX710B SCK | GPIO 22 |
| I²C (ADP810) SDA | GPIO 32 |
| I²C (ADP810) SCL | GPIO 33 |
| NTC Thermistor (ADC) | GPIO 34 |
| PZEM UART RX | GPIO 18 |
| PZEM UART TX | GPIO 19 |
| Relay | GPIO 5 |
| TFT SPI SDI | GPIO 13 |
| TFT SPI CLK | GPIO 14 |
| TFT CS | GPIO 15 |
| TFT DC | GPIO 25 |
| TFT RST | GPIO 26 |
| TFT LED | GPIO 0 |

A complete circuit diagram should be created using Fritzing, EasyEDA, or a similar tool for clarity.

- Code Explanation

Key Functions

- setup(): Initializes Wi-Fi, OTA, I²C, serial communication, sensors, and display.

- loop(): Continuously reads sensor values, updates the display, and sends data to APIs.

Sensor Reading Functions

- readNTCTemperature(): Converts analog NTC reading to temperature.

- readADP810Pressure(): Reads and calculates differential pressure from ADP810.

- readHX710B(): Measures air pressure from HX710B ADC module.

- getStableAnalogRead(): Averages analog readings for stability.

- pulseCounter(): ISR for counting water flow pulses.

Data Transmission

- Sends JSON data over HTTPS to ThingsBoard.

- Sends JSON with kit_id to Flask API over HTTP.

Display Output

- Uses TFT_22_ILI9225 library to draw values in formatted text.

- Setup and Usage Instructions

- Flash the Code: Upload the sketch using Arduino IDE or PlatformIO.

- Wi-Fi Setup: On first boot, ESP32 creates an AP named Plant_And_Machinery. Connect and set Wi-Fi credentials.

- Server Configuration: Ensure IPs and ports in the code match your ThingsBoard and Flask server setup.

- OTA Updates: Use Arduino IDE > Port > Network Ports > Select "Machinery" to upload wirelessly.

- View Data: Monitor the TFT display and remote dashboards.

- Data Flow and Communication

- Sensor Data Collection: All values are read every second.

- Display Update: Screen refreshes with the latest values.

- Secure Transmission: Encrypted POST request to ThingsBoard.

- Local Logging: Plain HTTP POST to Flask API with kit identifier.

- Troubleshooting and FAQs

❓ Q: TFT Display shows blank screen.

A:

- Check SPI wiring and power supply.

- Ensure tft.begin() is called and SPI pins match your wiring.

❓ Q: No Wi-Fi Connection.

A:

- Reset ESP32 to re-enter WiFiManager mode.

- Ensure your router allows new devices.

❓ Q: OTA fails.

A:

- Ensure the device and PC are on the same network.

- OTA is only available after a successful Wi-Fi connection.

❓ Q: PZEM values are NaN.

A:

- Confirm TX/RX wiring.

- Ensure the PZEM module is powered and connected correctly.

❓ Q: Sensor readings seem off.

A:

- Try recalibrating (e.g., zero offset or pressure baseline).

- Verify pull-up resistors and stable power supply.

- Sample Code

## Class 1: DHT11 + TFT Display

#include <WiFi.h>

#include <Wire.h>

#include <DHT.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

#define DHTPIN 4

#define DHTTYPE DHT11

DHT dht(DHTPIN, DHTTYPE);

void setup() {

Serial.begin(115200);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float temp = dht.readTemperature();

float hum = dht.readHumidity();

Serial.printf("Room Temp: %.2f C\nHumidity: %.2f %%\n", temp, hum);

tft.fillRectangle(0, 0, 176, 220, 0x0000); // Black background

tft.drawGFXText(5, 20, "Room Temp:", 0x07E0);  // Green

tft.drawGFXText(100, 20, String(temp, 1) + " C", 0xFFFF); // White

tft.drawGFXText(5, 50, "Humidity:", 0x07E0);

tft.drawGFXText(100, 50, String(hum, 1) + " %", 0xFFFF);

delay(2000);

}

Example output:

Room Temp: 24.30 C

Humidity: 48.50 %

## Class 2: NTC Thermistor + TFT Display

#include <WiFi.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#include <math.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define NTC_THERMISTOR_PIN 34

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define NUMSAMPLES 10

#define BCOEFFICIENT 3950

#define SERIESRESISTOR 10000

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

float readNTCTemperature() {

float avg = 0;

for (int i = 0; i < NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

void setup() {

Serial.begin(115200);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float temp = readNTCTemperature();

Serial.printf("Motor Temp: %.2f C\n", temp);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Motor Temp:", 0x07E0);

tft.drawGFXText(100, 20, String(temp, 1) + " C", 0xFFFF);

delay(2000);

}

Example output:

Motor Temp: 30.12 C

## Class 3: PZEM004T (Voltage, Current) + TFT Display

#include <WiFi.h>

#include <HardwareSerial.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#include <PZEM004Tv30.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

PZEM004Tv30 pzem(&Serial2, 18, 19);

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float voltage = pzem.voltage();

float current = pzem.current();

Serial.printf("Voltage: %.2f V\nCurrent: %.2f A\n", voltage, current);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Voltage:", 0x07E0);

tft.drawGFXText(100, 20, String(voltage, 2) + " V", 0xFFFF);

tft.drawGFXText(5, 50, "Current:", 0x07E0);

tft.drawGFXText(100, 50, String(current, 2) + " A", 0xFFFF);

delay(2000);

}

Example output:

Voltage: 230.45 V

Current: 0.85 A

## Class 4: ADP810 Differential Pressure + TFT Display

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define ADP810_ADDR 0x25

#define PRESSURE_THRESHOLD 1.0

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

long baselinePressure = 0;

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long diffPressure = Wire.read() << 8 | Wire.read();

Wire.read(); // checksum ignored for brevity

if (diffPressure & 0x8000) diffPressure -= 0x10000;

float result = (diffPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

void setup() {

Serial.begin(115200);

Wire.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

// Simple baseline calibration

baselinePressure = 0;

}

void loop() {

float pressure = readADP810Pressure();

Serial.printf("Diff Pressure: %.2f Pa\n", pressure);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Diff Pressure:", 0x07E0);

tft.drawGFXText(140, 20, String(pressure, 2) + " Pa", 0xFFFF);

delay(2000);

}

Example output:

Diff Pressure: 0.85 Pa

## Class 5: HX710B Air Pressure Sensor + TFT Display

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define HX710B_SCK 22

#define HX710B_OUT 21

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long zeroOffset = 0;

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

void setup() {

Serial.begin(115200);

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

// Calibrate zero offset

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

long airPressure = readHX710B();

Serial.printf("Air Pressure: %ld Pa\n", airPressure);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Air Pressure:", 0x07E0);

tft.drawGFXText(140, 20, String(airPressure) + " Pa", 0xFFFF);

delay(2000);

}

Example output:

Air Pressure: 123 Pa

## Class 6: DHT11 + NTC Thermistor + TFT Display

#include <WiFi.h>

#include <Wire.h>

#include <DHT.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#include <math.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define DHTPIN 4

#define DHTTYPE DHT11

DHT dht(DHTPIN, DHTTYPE);

#define NTC_THERMISTOR_PIN 34

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define NUMSAMPLES 10

#define BCOEFFICIENT 3950

#define SERIESRESISTOR 10000

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

float readNTCTemperature() {

float avg = 0;

for (int i = 0; i < NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

void setup() {

Serial.begin(115200);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float roomTemp = dht.readTemperature();

float hum = dht.readHumidity();

float motorTemp = readNTCTemperature();

Serial.printf("Room Temp: %.2f C, Humidity: %.2f %%\nMotor Temp: %.2f C\n", roomTemp, hum, motorTemp);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Room Temp:", 0x07E0);

tft.drawGFXText(100, 20, String(roomTemp, 1) + " C", 0xFFFF);

tft.drawGFXText(5, 50, "Humidity:", 0x07E0);

tft.drawGFXText(100, 50, String(hum, 1) + " %", 0xFFFF);

tft.drawGFXText(5, 80, "Motor Temp:", 0x07E0);

tft.drawGFXText(110, 80, String(motorTemp, 1) + " C", 0xFFFF);

delay(2500);

}

Example output:

Room Temp: 23.95 C, Humidity: 48.20 %

Motor Temp: 29.50 C

## Class 7: PZEM004T + ADP810 Differential Pressure + TFT Display

#include <WiFi.h>

#include <HardwareSerial.h>

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#include <PZEM004Tv30.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define ADP810_ADDR 0x25

#define PRESSURE_THRESHOLD 1.0

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

PZEM004Tv30 pzem(&Serial2, 18, 19);

long baselinePressure = 0;

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long diffPressure = Wire.read() << 8 | Wire.read();

Wire.read(); // checksum ignored

if (diffPressure & 0x8000) diffPressure -= 0x10000;

float result = (diffPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

Wire.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

baselinePressure = 0;

}

void loop() {

float voltage = pzem.voltage();

float current = pzem.current();

float diffPressure = readADP810Pressure();

Serial.printf("Voltage: %.2f V, Current: %.2f A\nDiff Pressure: %.2f Pa\n", voltage, current, diffPressure);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Voltage:", 0x07E0);

tft.drawGFXText(100, 20, String(voltage, 2) + " V", 0xFFFF);

tft.drawGFXText(5, 50, "Current:", 0x07E0);

tft.drawGFXText(100, 50, String(current, 2) + " A", 0xFFFF);

tft.drawGFXText(5, 80, "Diff Pressure:", 0x07E0);

tft.drawGFXText(140, 80, String(diffPressure, 2) + " Pa", 0xFFFF);

delay(2500);

}

Example output:

Voltage: 230.40 V, Current: 0.87 A

Diff Pressure: 0.92 Pa

## Class 8: HX710B + Flow Sensor + TFT Display

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define HX710B_SCK 22

#define HX710B_OUT 21

#define FLOW_SENSOR_PIN 23

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile uint32_t flowCount = 0;

void IRAM_ATTR flowISR() {

flowCount++;

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long zeroOffset = 0;

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

void setup() {

Serial.begin(115200);

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

pinMode(FLOW_SENSOR_PIN, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR_PIN), flowISR, RISING);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

static uint32_t lastFlowCount = 0;

static uint32_t lastMillis = 0;

long airPressure = readHX710B();

uint32_t now = millis();

if (now - lastMillis >= 1000) {

uint32_t pulses = flowCount - lastFlowCount;

float flowRate = pulses * 2.25; // Example flow rate conversion

lastFlowCount = flowCount;

lastMillis = now;

Serial.printf("Air Pressure: %ld Pa\nFlow Rate: %.2f L/min\n", airPressure, flowRate);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Air Pressure:", 0x07E0);

tft.drawGFXText(140, 20, String(airPressure) + " Pa", 0xFFFF);

tft.drawGFXText(5, 50, "Flow Rate:", 0x07E0);

tft.drawGFXText(110, 50, String(flowRate, 2) + " L/min", 0xFFFF);

}

delay(100);

}

Example output:

Air Pressure: 125 Pa

Flow Rate: 3.38 L/min

## Class 9: DHT11 + PZEM004T + Relay Status + TFT Display

#include <WiFi.h>

#include <HardwareSerial.h>

#include <DHT.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#include <PZEM004Tv30.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define DHTPIN 4

#define DHTTYPE DHT11

DHT dht(DHTPIN, DHTTYPE);

#define RELAY_PIN 5

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

PZEM004Tv30 pzem(&Serial2, 18, 19);

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

pinMode(RELAY_PIN, OUTPUT);

digitalWrite(RELAY_PIN, LOW);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float roomTemp = dht.readTemperature();

float hum = dht.readHumidity();

float voltage = pzem.voltage();

float current = pzem.current();

bool relayState = digitalRead(RELAY_PIN);

Serial.printf("Room Temp: %.2f C, Humidity: %.2f %%\nVoltage: %.2f V, Current: %.2f A\nRelay: %s\n",

roomTemp, hum, voltage, current, relayState ? "ON" : "OFF");

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Room Temp:", 0x07E0);

tft.drawGFXText(100, 20, String(roomTemp, 1) + " C", 0xFFFF);

tft.drawGFXText(5, 50, "Humidity:", 0x07E0);

tft.drawGFXText(100, 50, String(hum, 1) + " %", 0xFFFF);

tft.drawGFXText(5, 80, "Voltage:", 0x07E0);

tft.drawGFXText(100, 80, String(voltage, 2) + " V", 0xFFFF);

tft.drawGFXText(5, 110, "Current:", 0x07E0);

tft.drawGFXText(100, 110, String(current, 2) + " A", 0xFFFF);

tft.drawGFXText(5, 140, "Relay:", 0x07E0);

tft.drawGFXText(60, 140, relayState ? "ON" : "OFF", 0xFFFF);

delay(3000);

}

Example output:

Room Temp: 23.90 C, Humidity: 47.80 %

Voltage: 230.50 V, Current: 0.88 A

Relay: OFF

## Class 10: ADP810 + HX710B + Flow Sensor + TFT Display

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

#define ADP810_ADDR 0x25

#define PRESSURE_THRESHOLD 1.0

#define HX710B_SCK 22

#define HX710B_OUT 21

#define FLOW_SENSOR_PIN 23

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile uint32_t flowCount = 0;

void IRAM_ATTR flowISR() {

flowCount++;

}

long baselinePressure = 0;

long zeroOffset = 0;

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long diffPressure = Wire.read() << 8 | Wire.read();

Wire.read(); // checksum ignored

if (diffPressure & 0x8000) diffPressure -= 0x10000;

float result = (diffPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

void setup() {

Serial.begin(115200);

Wire.begin();

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

pinMode(FLOW_SENSOR_PIN, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR_PIN), flowISR, RISING);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

baselinePressure = 0;

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

static uint32_t lastFlowCount = 0;

static uint32_t lastMillis = 0;

float diffPressure = readADP810Pressure();

long airPressure = readHX710B();

uint32_t now = millis();

if (now - lastMillis >= 1000) {

uint32_t pulses = flowCount - lastFlowCount;

float flowRate = pulses * 2.25;

lastFlowCount = flowCount;

lastMillis = now;

Serial.printf("Diff Pressure: %.2f Pa\nAir Pressure: %ld Pa\nFlow Rate: %.2f L/min\n", diffPressure, airPressure, flowRate);

tft.fillRectangle(0, 0, 176, 220, 0x0000);

tft.drawGFXText(5, 20, "Diff Pressure:", 0x07E0);

tft.drawGFXText(140, 20, String(diffPressure, 2) + " Pa", 0xFFFF);

tft.drawGFXText(5, 50, "Air Pressure:", 0x07E0);

tft.drawGFXText(140, 50, String(airPressure) + " Pa", 0xFFFF);

tft.drawGFXText(5, 80, "Flow Rate:", 0x07E0);

tft.drawGFXText(110, 80, String(flowRate, 2) + " L/min", 0xFFFF);

}

delay(100);

}

Example output:

Diff Pressure: 0.82 Pa

Air Pressure: 130 Pa

Flow Rate: 4.50 L/min

## Class 11: DHT11 + ADP810 Pressure + TFT Display

#include <Wire.h>

#include <DHT.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define DHTPIN 4

#define DHTTYPE DHT11

#define ADP810_ADDR 0x25

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

DHT dht(DHTPIN, DHTTYPE);

long baselinePressure = 0;

long differentialPressure = 0;

const float PRESSURE_THRESHOLD = 1;

void setup() {

Serial.begin(115200);

Wire.begin(32, 33);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

calibrateSensor();

}

void loop() {

float roomTemp = dht.readTemperature();

float humidity = dht.readHumidity();

float diffPressure = readADP810Pressure();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Room Temp:", isnan(roomTemp) ? "---" : String(roomTemp, 1) + " C", 20);

displayRow("Humidity:", isnan(humidity) ? "---" : String(humidity, 0) + " %", 40);

displayRow("Diff Pres:", String(diffPressure, 2) + " Pa", 60);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color = COLOR_WHITE) {

int labelX = 5, valueX = 100;

tft.drawGFXText(labelX, y, label, COLOR_CYAN);

tft.drawGFXText(valueX, y, value, color);

}

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

differentialPressure = Wire.read() << 8 | Wire.read();

if (differentialPressure & 0x8000) differentialPressure -= 0x10000;

float result = (differentialPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

void calibrateSensor() {

long sum = 0;

for (int i = 0; i < 100; i++) {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long p = Wire.read() << 8 | Wire.read();

if (p & 0x8000) p -= 0x10000;

sum += p;

}

delay(10);

}

baselinePressure = sum / 100;

}

Output on TFT Display:

Room Temp: 26.5 C

Humidity: 55 %

Diff Pres: 1.23 Pa

## Class 12: NTC Thermistor + Flow Sensor + TFT Display

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define NTC_THERMISTOR_PIN 34

#define SERIESRESISTOR 10000

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define BCOEFFICIENT 3950

#define NUMSAMPLES 10

#define FLOW_SENSOR 17

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile int pulseCount = 0;

unsigned long lastFlowTime = 0;

float flowRate = 0;

void IRAM_ATTR pulseCounter() {

pulseCount++;

}

void setup() {

Serial.begin(115200);

pinMode(FLOW_SENSOR, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR), pulseCounter, RISING);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

if (millis() - lastFlowTime >= 1000) {

noInterrupts();

flowRate = (pulseCount / 7.5);

pulseCount = 0;

interrupts();

lastFlowTime = millis();

}

float ntcTemp = readNTCTemperature();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("NTC Temp:", String(ntcTemp, 1) + " C", 20);

displayRow("Flow Rate:", String(flowRate, 1) + " L/min", 40);

delay(1000);

}

void displayRow(String label, String value, int y, uint16_t color = COLOR_WHITE) {

int labelX = 5, valueX = 100;

tft.drawGFXText(labelX, y, label, COLOR_CYAN);

tft.drawGFXText(valueX, y, value, color);

}

float readNTCTemperature() {

float avg = 0;

for (int i = 0; i < NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

Output on TFT Display:

NTC Temp: 29.5 C

Flow Rate: 4.0 L/min

## Class 13: PZEM004T Energy Monitor + DHT11 + TFT Display

#include <DHT.h>

#include <PZEM004Tv30.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define DHTPIN 4

#define DHTTYPE DHT11

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

DHT dht(DHTPIN, DHTTYPE);

PZEM004Tv30 pzem(&Serial2, 18, 19);

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

float roomTemp = dht.readTemperature();

float humidity = dht.readHumidity();

float voltage = pzem.voltage();

float current = pzem.current();

float power = pzem.power();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Room Temp:", isnan(roomTemp) ? "---" : String(roomTemp, 1) + " C", 20);

displayRow("Humidity:", isnan(humidity) ? "---" : String(humidity, 0) + " %", 40);

displayRow("Voltage:", isnan(voltage) ? "---" : String(voltage, 2) + " V", 60);

displayRow("Current:", isnan(current) ? "---" : String(current, 2) + " A", 80);

displayRow("Power:", isnan(power) ? "---" : String(power, 2) + " W", 100);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color = COLOR_WHITE) {

int labelX = 5, valueX = 100;

tft.drawGFXText(labelX, y, label, COLOR_CYAN);

tft.drawGFXText(valueX, y, value, color);

}

Output on TFT Display:

Room Temp: 27.8 C

Humidity: 48 %

Voltage: 230.50 V

Current: 1.25 A

Power: 287.5 W

## Class 14: HX710B Pressure Sensor + Flow Sensor + TFT Display

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define FLOW_SENSOR 17

#define HX710B_SCK 22

#define HX710B_OUT 21

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile int pulseCount = 0;

unsigned long lastFlowTime = 0;

float flowRate = 0;

void IRAM_ATTR pulseCounter() {

pulseCount++;

}

long zeroOffset = 0;

void setup() {

Serial.begin(115200);

pinMode(FLOW_SENSOR, INPUT_PULLUP);

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR), pulseCounter, RISING);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

Serial.println("Calibrating HX710B...");

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

if (millis() - lastFlowTime >= 1000) {

noInterrupts();

flowRate = (pulseCount / 7.5);

pulseCount = 0;

interrupts();

lastFlowTime = millis();

}

long airPressure = readHX710B();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Flow Rate:", String(flowRate, 1) + " L/min", 20);

displayRow("Air Pressure:", String(airPressure) + " Pa", 40);

delay(1000);

}

void displayRow(String label, String value, int y, uint16_t color = COLOR_WHITE) {

int labelX = 5, valueX = 100;

tft.drawGFXText(labelX, y, label, COLOR_CYAN);

tft.drawGFXText(valueX, y, value, color);

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

Output on TFT Display:

Flow Rate: 3.80 L/min

Air Pressure: 150 Pa

## Class 15: NTC Thermistor + HX710B + TFT Display

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define NTC_THERMISTOR_PIN 34

#define SERIESRESISTOR 10000

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define BCOEFFICIENT 3950

#define NUMSAMPLES 10

#define HX710B_SCK 22

#define HX710B_OUT 21

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

long zeroOffset = 0;

void setup() {

Serial.begin(115200);

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

Serial.println("Calibrating HX710B...");

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

float ntcTemp = readNTCTemperature();

long airPressure = readHX710B();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("NTC Temp:", String(ntcTemp, 1) + " C", 20);

displayRow("Air Pressure:", String(airPressure) + " Pa", 40);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color = COLOR_WHITE) {

int labelX = 5, valueX = 100;

tft.drawGFXText(labelX, y, label, COLOR_CYAN);

tft.drawGFXText(valueX, y, value, color);

}

float readNTCTemperature() {

float avg = 0;

for (int i = 0; i < NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

Output on TFT Display:

NTC Temp: 30.2 C

Air Pressure: 140 Pa

## Class 16: DHT11 + PZEM004T + Flow Sensor + TFT Display

#include <DHT.h>

#include <PZEM004Tv30.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define DHTPIN 4

#define DHTTYPE DHT11

#define FLOW_SENSOR 17

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

DHT dht(DHTPIN, DHTTYPE);

PZEM004Tv30 pzem(&Serial2, 18, 19);

volatile int pulseCount = 0;

unsigned long lastFlowTime = 0;

float flowRate = 0;

void IRAM_ATTR pulseCounter() {

pulseCount++;

}

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

pinMode(FLOW_SENSOR, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR), pulseCounter, RISING);

dht.begin();

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

}

void loop() {

if (millis() - lastFlowTime >= 1000) {

noInterrupts();

flowRate = pulseCount / 7.5;

pulseCount = 0;

interrupts();

lastFlowTime = millis();

}

float roomTemp = dht.readTemperature();

float humidity = dht.readHumidity();

float voltage = pzem.voltage();

float current = pzem.current();

float power = pzem.power();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Room Temp:", isnan(roomTemp) ? "---" : String(roomTemp,1)+" C", 20);

displayRow("Humidity:", isnan(humidity) ? "---" : String(humidity,0)+" %", 40);

displayRow("Flow Rate:", String(flowRate,1)+" L/min", 60);

displayRow("Voltage:", isnan(voltage) ? "---" : String(voltage,2)+" V", 80);

displayRow("Current:", isnan(current) ? "---" : String(current,2)+" A", 100);

displayRow("Power:", isnan(power) ? "---" : String(power,2)+" W", 120);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color=COLOR_WHITE) {

int labelX=5, valueX=100;

tft.drawGFXText(labelX,y,label,COLOR_CYAN);

tft.drawGFXText(valueX,y,value,color);

}

Output on TFT Display:

Room Temp: 27.0 C

Humidity: 52 %

Flow Rate: 4.2 L/min

Voltage: 231.10 V

Current: 1.10 A

Power: 254.3 W

## Class 17: NTC Thermistor + ADP810 + Flow Sensor + TFT Display

#include <Wire.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define NTC_THERMISTOR_PIN 34

#define SERIESRESISTOR 10000

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define BCOEFFICIENT 3950

#define NUMSAMPLES 10

#define FLOW_SENSOR 17

#define ADP810_ADDR 0x25

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile int pulseCount = 0;

unsigned long lastFlowTime = 0;

float flowRate = 0;

long baselinePressure = 0;

const float PRESSURE_THRESHOLD = 1;

void IRAM_ATTR pulseCounter() {

pulseCount++;

}

void setup() {

Serial.begin(115200);

pinMode(FLOW_SENSOR, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR), pulseCounter, RISING);

Wire.begin(32, 33);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

calibrateSensor();

}

void loop() {

if (millis() - lastFlowTime >= 1000) {

noInterrupts();

flowRate = pulseCount / 7.5;

pulseCount = 0;

interrupts();

lastFlowTime = millis();

}

float ntcTemp = readNTCTemperature();

float diffPressure = readADP810Pressure();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("NTC Temp:", String(ntcTemp,1)+" C", 20);

displayRow("Diff Pres:", String(diffPressure,2)+" Pa", 40);

displayRow("Flow Rate:", String(flowRate,1)+" L/min", 60);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color=COLOR_WHITE) {

int labelX=5, valueX=100;

tft.drawGFXText(labelX,y,label,COLOR_CYAN);

tft.drawGFXText(valueX,y,value,color);

}

float readNTCTemperature() {

float avg=0;

for(int i=0; i<NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long differentialPressure = Wire.read() << 8 | Wire.read();

if (differentialPressure & 0x8000) differentialPressure -= 0x10000;

float result = (differentialPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

void calibrateSensor() {

long sum = 0;

for (int i=0; i<100; i++) {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long p = Wire.read() << 8 | Wire.read();

if (p & 0x8000) p -= 0x10000;

sum += p;

}

delay(10);

}

baselinePressure = sum / 100;

}

Output on TFT Display:

CopyEdit

NTC Temp: 28.8 C

Diff Pres: 1.15 Pa

Flow Rate: 3.7 L/min

## Class 18: DHT11 + HX710B + PZEM004T + TFT Display

#include <DHT.h>

#include <PZEM004Tv30.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define DHTPIN 4

#define DHTTYPE DHT11

#define HX710B_SCK 22

#define HX710B_OUT 21

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

DHT dht(DHTPIN, DHTTYPE);

PZEM004Tv30 pzem(&Serial2, 18, 19);

long zeroOffset = 0;

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

dht.begin();

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

Serial.println("Calibrating HX710B...");

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

float roomTemp = dht.readTemperature();

float humidity = dht.readHumidity();

long airPressure = readHX710B();

float voltage = pzem.voltage();

float current = pzem.current();

float power = pzem.power();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Room Temp:", isnan(roomTemp) ? "---" : String(roomTemp,1)+" C", 20);

displayRow("Humidity:", isnan(humidity) ? "---" : String(humidity,0)+" %", 40);

displayRow("Air Pressure:", String(airPressure)+" Pa", 60);

displayRow("Voltage:", isnan(voltage) ? "---" : String(voltage,2)+" V", 80);

displayRow("Current:", isnan(current) ? "---" : String(current,2)+" A", 100);

displayRow("Power:", isnan(power) ? "---" : String(power,2)+" W", 120);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color=COLOR_WHITE) {

int labelX=5, valueX=100;

tft.drawGFXText(labelX,y,label,COLOR_CYAN);

tft.drawGFXText(valueX,y,value,color);

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

Output on TFT Display:

Room Temp: 26.4 C

Humidity: 49 %

Air Pressure: 135 Pa

Voltage: 229.90 V

Current: 1.30 A

Power: 300.2 W

## Class 19: ADP810 + Flow Sensor + PZEM004T + TFT Display

#include <Wire.h>

#include <PZEM004Tv30.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define FLOW_SENSOR 17

#define ADP810_ADDR 0x25

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

volatile int pulseCount = 0;

unsigned long lastFlowTime = 0;

float flowRate = 0;

long baselinePressure = 0;

const float PRESSURE_THRESHOLD = 1;

PZEM004Tv30 pzem(&Serial2, 18, 19);

void IRAM_ATTR pulseCounter() {

pulseCount++;

}

void setup() {

Serial.begin(115200);

Serial2.begin(9600, SERIAL_8N1, 18, 19);

pinMode(FLOW_SENSOR, INPUT_PULLUP);

attachInterrupt(digitalPinToInterrupt(FLOW_SENSOR), pulseCounter, RISING);

Wire.begin(32, 33);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

calibrateSensor();

}

void loop() {

if (millis() - lastFlowTime >= 1000) {

noInterrupts();

flowRate = pulseCount / 7.5;

pulseCount = 0;

interrupts();

lastFlowTime = millis();

}

float diffPressure = readADP810Pressure();

float voltage = pzem.voltage();

float current = pzem.current();

float power = pzem.power();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Diff Pres:", String(diffPressure,2)+" Pa", 20);

displayRow("Flow Rate:", String(flowRate,1)+" L/min", 40);

displayRow("Voltage:", isnan(voltage) ? "---" : String(voltage,2)+" V", 60);

displayRow("Current:", isnan(current) ? "---" : String(current,2)+" A", 80);

displayRow("Power:", isnan(power) ? "---" : String(power,2)+" W", 100);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color=COLOR_WHITE) {

int labelX=5, valueX=100;

tft.drawGFXText(labelX,y,label,COLOR_CYAN);

tft.drawGFXText(valueX,y,value,color);

}

float readADP810Pressure() {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long differentialPressure = Wire.read() << 8 | Wire.read();

if (differentialPressure & 0x8000) differentialPressure -= 0x10000;

float result = (differentialPressure - baselinePressure) / 60.0;

return abs(result) < PRESSURE_THRESHOLD ? 0.0 : result;

}

return 0.0;

}

void calibrateSensor() {

long sum = 0;

for (int i=0; i<100; i++) {

Wire.beginTransmission(ADP810_ADDR);

Wire.write(0x37); Wire.write(0x2D);

Wire.endTransmission();

delay(10);

Wire.requestFrom(ADP810_ADDR, 7);

if (Wire.available() == 7) {

long p = Wire.read() << 8 | Wire.read();

if (p & 0x8000) p -= 0x10000;

sum += p;

}

delay(10);

}

baselinePressure = sum / 100;

}

Output on TFT Display:

Diff Pres: 1.10 Pa

Flow Rate: 3.8 L/min

Voltage: 230.10 V

Current: 1.12 A

Power: 258.3 W

## Class 20: DHT11 + NTC Thermistor + HX710B + TFT Display

#include <DHT.h>

#include "SPI.h"

#include "TFT_22_ILI9225.h"

#include <../fonts/FreeSans9pt7b.h>

#define DHTPIN 4

#define DHTTYPE DHT11

#define NTC_THERMISTOR_PIN 34

#define SERIESRESISTOR 10000

#define THERMISTORNOMINAL 10000

#define TEMPERATURENOMINAL 25

#define BCOEFFICIENT 3950

#define NUMSAMPLES 10

#define HX710B_SCK 22

#define HX710B_OUT 21

#define TFT_RST 26

#define TFT_RS  25

#define TFT_CS  15

#define TFT_SDI 13

#define TFT_CLK 14

#define TFT_LED 0

#define TFT_BRIGHTNESS 200

SPIClass hspi(HSPI);

TFT_22_ILI9225 tft = TFT_22_ILI9225(TFT_RST, TFT_RS, TFT_CS, TFT_LED, TFT_BRIGHTNESS);

DHT dht(DHTPIN, DHTTYPE);

long zeroOffset = 0;

void setup() {

Serial.begin(115200);

dht.begin();

pinMode(HX710B_SCK, OUTPUT);

pinMode(HX710B_OUT, INPUT);

hspi.begin();

tft.begin(hspi);

tft.clear();

tft.setGFXFont(&FreeSans9pt7b);

Serial.println("Calibrating HX710B...");

delay(2000);

zeroOffset = readHX710B_raw();

}

void loop() {

float roomTemp = dht.readTemperature();

float humidity = dht.readHumidity();

float ntcTemp = readNTCTemperature();

long airPressure = readHX710B();

tft.fillRectangle(0, 0, 176, 220, COLOR_BLACK);

displayRow("Room Temp:", isnan(roomTemp) ? "---" : String(roomTemp,1)+" C", 20);

displayRow("Humidity:", isnan(humidity) ? "---" : String(humidity,0)+" %", 40);

displayRow("NTC Temp:", String(ntcTemp,1)+" C", 60);

displayRow("Air Pressure:", String(airPressure)+" Pa", 80);

delay(2000);

}

void displayRow(String label, String value, int y, uint16_t color=COLOR_WHITE) {

int labelX=5, valueX=100;

tft.drawGFXText(labelX,y,label,COLOR_CYAN);

tft.drawGFXText(valueX,y,value,color);

}

float readNTCTemperature() {

float avg=0;

for(int i=0; i<NUMSAMPLES; i++) {

avg += analogRead(NTC_THERMISTOR_PIN);

delay(5);

}

avg /= NUMSAMPLES;

float voltage = avg * (3.3 / 4095.0);

float resistance = SERIESRESISTOR / ((3.3 / voltage) - 1);

float temp = resistance / THERMISTORNOMINAL;

temp = log(temp);

temp /= BCOEFFICIENT;

temp += 1.0 / (TEMPERATURENOMINAL + 273.15);

temp = 1.0 / temp;

return temp - 273.15;

}

long readHX710B_raw() {

long count = 0;

while (digitalRead(HX710B_OUT));

for (int i = 0; i < 24; i++) {

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

count <<= 1;

digitalWrite(HX710B_SCK, LOW); delayMicroseconds(1);

if (digitalRead(HX710B_OUT)) count++;

}

digitalWrite(HX710B_SCK, HIGH); delayMicroseconds(1);

digitalWrite(HX710B_SCK, LOW);

if (count & 0x800000) count |= ~0xFFFFFF;

return count / 100;

}

long readHX710B() {

long raw = readHX710B_raw();

long adjusted = raw - zeroOffset;

return abs(adjusted) < 20 ? 0 : adjusted;

}

Output on TFT Display:

Room Temp: 27.1 C

Humidity: 50 %

NTC Temp: 29.0 C

Air Pressure: 140 Pa